## Hydraulic Calculation
www.nsvsoft.net
Enter Values in Green Cells | [6 empty] | Most Remote Sprinkler
Select Values of Blue Cells | [6 empty] | Area of Coverage (ft²) |  |  | 110
Last node shall be "Test" | [6 empty] | Desnsity (gpm/ft²) |  |  | 0.2
Node 1 | Elev 1 (ft) | K Factor | Flow | Hose Stream Allowance (gpm) | Pipe Type | Nominal ID | Fitting(s) Eqv. Length (ft) | L (ft) | C Factor | Total (Pt)
Node 2 | Elev 2 (ft) |  | Tot. Flow |  |  | Actual ID |  | F (ft) | Pf (psi/ft) | Elev (Pe)
[8 empty] | T (ft) |  | Frict (pf)
101 | 9 | 8 | 22 | 0 | SCH40 | 1 | 0 | 12 | 120 | 7.5625
102 | 9 |  | 22 |  |  | 1.049 | 0 | 0 | 0.15522 | 0
[7 empty] | 0 | 12 |  | 1.8627
102 | 9 | 8 | 24.5604 | 0 | SCH40 | 1.25 | 0 | 12 | 120 | 9.4252
103 | 9 |  | 46.5604 |  |  | 1.38 | 0 | 0 | 0.16341 | 0
[7 empty] | 0 | 12 |  | 1.9609
103 | 9 | 8 | 26.9946 | 0 | SCH40 | 1.5 | 4 | 18 | 120 | 11.3861
C1 | 8 |  | 73.555 |  |  | 1.61 | 8 | 12 | 0.17974 | 0.433
[7 empty] | 0 | 30 |  | 5.3922
C1 | 8 | 0 | 0 | 0 | SCH10 | 2 | 0 | 10 | 120 | 17.2113
C2 | 8 |  | 73.555 |  |  | 2.157 | 0 | 0 | 0.043255 | 0
[7 empty] | 0 | 10 |  | 0.43255
C2 | 8 | 17.81 | 74.8101 | 0 | SCH10 | 2 | 0 | 10 | 120 | 17.6438
C3 | 8 |  | 148.3651 |  |  | 2.157 | 0 | 0 | 0.1584 | 0
[7 empty] | 0 | 10 |  | 1.584
C3 | 8 | 14.02 | 61.4771 | 0 | SCH10 | 2 | 0 | 10 | 120 | 19.2279
C4 | 8 |  | 209.8422 |  |  | 2.157 | 0 | 0 | 0.30082 | 0
[7 empty] | 0 | 10 |  | 3.0082
C4 | 8 | 0 | 0 | 0 | SCH10 | 2.5 | 8.2 | 44 | 120 | 22.236
C5 | 8 |  | 209.8422 |  |  | 2.635 | 0 | 8.2 | 0.11349 | 0
[7 empty] | 0 | 52.2 |  | 5.9241
C5 | 8 | 0 | 0 | 0 | SCH10 | 2.5 | 19.2 | 7 | 120 | 28.1602
C6 | 1 |  | 209.8422 |  |  | 2.635 | 1.4 | 20.6 | 0.11349 | 3.031
[7 empty] | 0 | 27.6 |  | 3.1323
C6 | 1 | 0 | 0 | 0 | CMNTLND52 | 3 | 9.2 | 100 | 120 | 34.3234
Test | 2 |  | 209.8422 |  |  | 3.28 | 27.6 | 36.8 | 0.039071 | -0.433
[7 empty] | 0 | 136.8 |  | 5.3448
Test | 2 | 0 | 209.8422 | 250 | SCH40 | 3 | 0 | 0 | 120 | 39.2353
0 | 0 |  | 459.8422 |  |  | 3.068 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 200 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | CMNTLND52 | 6 | 0 | 0 | 0
0 | 0 |  |  |  |  | 6.16 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
0 | 0 | 0 |  | 0 | SCH10 | 1 | 0 | 0 | 0
0 | 0 |  |  |  |  | 1.097 | 0 | 0
[7 empty] | 0 | 0
[12 empty] | 40 | SCH40a: |  | 10 | SCH10a:
[12 empty] | 1 | 1.049 |  | 1 | 1.097
[12 empty] | 1.25 | 1.38 |  | 1.25 | 1.442
[12 empty] | 1.5 | 1.61 |  | 1.5 | 1.682
[12 empty] | 2 | 2.067 |  | 2 | 2.157
[12 empty] | 2.5 | 2.469 |  | 2.5 | 2.635
[12 empty] | 3 | 3.068 |  | 3 | 3.26
[12 empty] | 3.5 | 3.548 |  | 3.5 | 3.76
[12 empty] | 4 | 4.026 |  | 4 | 4.26
[12 empty] | 5 | 5.047 |  | 5 | 5.295
[12 empty] | 6 | 6.065 |  | 6 | 6.357
[12 empty] | 8 | 7.981 |  | 8 | 8.249
[13 empty] | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
[12 empty] | SCH 10 | 0.674 | 0.884 | 1.097 | 1.442 | 1.682 | 2.157 | 2.635 | 3.26 | 3.76 | 4.26 | 5.295 | 6.357 | 8.249 | 10.37 | 12.09 | 64.212
[12 empty] | SCH 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.071 | 10.14 | 0 | 18.211
[12 empty] | SCH 40 | 0.622 | 0.824 | 1.049 | 1.38 | 1.61 | 2.067 | 2.469 | 3.068 | 3.548 | 4.026 | 5.047 | 6.065 | 7.981 | 10.02 | 11.938 | 61.714
[12 empty] | Copper- Type K | 0 | 0.745 | 0.995 | 1.245 | 1.481 | 1.959 | 2.435 | 2.907 | 3.385 | 3.857 | 4.805 | 5.741 | 7.583 | 9.449 | 0 | 46.587
[12 empty] | Copper- Type L | 0 | 0.785 | 1.025 | 1.265 | 1.505 | 1.985 | 2.465 | 2.945 | 3.425 | 3.905 | 4.875 | 5.845 | 7.725 | 9.625 | 0 | 47.375
[12 empty] | Copper- Type M | 0 | 0.811 | 1.055 | 1.291 | 1.527 | 2.009 | 2.495 | 2.981 | 3.459 | 3.935 | 4.907 | 5.881 | 7.785 | 9.701 | 0 | 47.837
[12 empty] | CPVC | 0 | 0.874 | 1.101 | 1.394 | 1.598 | 2.003 | 2.423 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.343
[12 empty] | SCH 10 |  |  | SCH 30 |  |  | SCH 40 |  |  | Copper- Type K |  |  | Copper- Type L |  |  |  | Copper- Type M |  | CPVC |  | Cement Lined-Ductil Iron-52
[11 empty] | 0.5 | 0.674 |  | 0.5 | 0 |  | 0.5 | 0.622 |  | 0.5 | 0 |  | 0.5 | 0 |  |  | 0.5 | 0 | 0.5 | 0 | 0.5 | 0
[11 empty] | 0.75 | 0.884 |  | 0.75 | 0 |  | 0.75 | 0.824 |  | 0.75 | 0.745 |  | 0.75 | 0.785 |  |  | 0.75 | 0.811 | 0.75 | 0.874 | 0.75 | 0
[11 empty] | 1 | 1.097 |  | 1 | 0 |  | 1 | 1.049 |  | 1 | 0.995 |  | 1 | 1.025 |  |  | 1 | 1.055 | 1 | 1.101 | 1 | 0
[11 empty] | 1.25 | 1.442 |  | 1.25 | 0 |  | 1.25 | 1.38 |  | 1.25 | 1.245 |  | 1.25 | 1.265 |  |  | 1.25 | 1.291 | 1.25 | 1.394 | 1.25 | 0
[11 empty] | 1.5 | 1.682 |  | 1.5 | 0 |  | 1.5 | 1.61 |  | 1.5 | 1.481 |  | 1.5 | 1.505 |  |  | 1.5 | 1.527 | 1.5 | 1.598 | 1.5 | 0
[11 empty] | 2 | 2.157 |  | 2 | 0 |  | 2 | 2.067 |  | 2 | 1.959 |  | 2 | 1.985 |  |  | 2 | 2.009 | 2 | 2.003 | 2 | 0
[11 empty] | 2.5 | 2.635 |  | 2.5 | 0 |  | 2.5 | 2.469 |  | 2.5 | 2.435 |  | 2.5 | 2.465 |  |  | 2.5 | 2.495 | 2.5 | 2.423 | 2.5 | 0
[11 empty] | 3 | 3.26 |  | 3 | 0 |  | 3 | 3.068 |  | 3 | 2.907 |  | 3 | 2.945 |  |  | 3 | 2.981 | 3 | 2.95 | 3 | 3.28
[11 empty] | 3.5 | 3.76 |  | 3.5 | 0 |  | 3.5 | 6.548 |  | 3.5 | 3.385 |  | 3.5 | 3.425 |  |  | 3.5 | 3.459 | 3.5 | 0 | 3.5 | 0
[11 empty] | 4 | 4.26 |  | 4 | 0 |  | 4 | 4.026 |  | 4 | 3.857 |  | 4 | 3.905 |  |  | 4 | 3.935 | 4 | 0 | 4 | 4.16
[11 empty] | 5 | 5.295 |  | 5 | 0 |  | 5 | 5.047 |  | 5 | 4.805 |  | 5 | 4.875 |  |  | 5 | 4.907 | 5 | 0 | 5 | 0
[11 empty] | 6 | 6.357 |  | 6 | 0 |  | 6 | 6.065 |  | 6 | 5.741 |  | 6 | 5.845 |  |  | 6 | 5.881 | 6 | 0 | 6 | 6.28
[11 empty] | 8 | 8.249 |  | 8 | 8.071 |  | 8 | 7.981 |  | 8 | 7.583 |  | 8 | 7.725 |  |  | 8 | 7.785 | 8 | 0 | 8 | 8.39
[11 empty] | 10 | 10.37 |  | 10 | 10.14 |  | 10 | 10.02 |  | 10 | 9.449 |  | 10 | 9.625 |  |  | 10 | 9.701 | 10 | 0 | 10 | 10.4
[11 empty] | 12 | 12.09 |  | 12 | 0 |  | 12 | 11.938 |  | 12 | 0 |  | 12 | 0 |  |  | 12 | 0 | 12 | 0 | 12 | 12.46
SCH 30
[11 empty] | 8 | 8.071
[11 empty] | 10 | 10.14
[11 empty] | 12 | 0
SCH 40
[11 empty] | 0.5 | 0.622
[11 empty] | 0.75 | 0.824
[11 empty] | 1 | 1.049
[11 empty] | 1.25 | 1.38
[11 empty] | 1.5 | 1.61
[11 empty] | 2 | 2.067
[11 empty] | 2.5 | 2.469
[11 empty] | 3 | 3.068
[11 empty] | 3.5 | 3.548
[11 empty] | 4 | 4.026
[11 empty] | 5 | 5.047
[11 empty] | 6 | 6.065
[11 empty] | 8 | 7.981
[11 empty] | 10 | 10.02
[11 empty] | 12 | 11.938
Copper- Type K
[11 empty] | 0.75 | 0.745
[11 empty] | 1 | 0.995
[11 empty] | 1.25 | 1.245
[11 empty] | 1.5 | 1.481
[11 empty] | 2 | 1.959
[11 empty] | 2.5 | 2.435
[11 empty] | 3 | 2.907
[11 empty] | 3.5 | 3.385
[11 empty] | 4 | 3.857
[11 empty] | 5 | 4.805
[11 empty] | 6 | 5.741
[11 empty] | 8 | 7.583
[11 empty] | 10 | 9.449
Copper- Type L
[11 empty] | 0.75 | 0.785
[11 empty] | 1 | 1.025
[11 empty] | 1.25 | 1.265
[11 empty] | 1.5 | 1.505
[11 empty] | 2 | 1.985
[11 empty] | 2.5 | 2.465
[11 empty] | 3 | 2.945
[11 empty] | 3.5 | 3.425
[11 empty] | 4 | 3.905
[11 empty] | 5 | 4.875
[11 empty] | 6 | 5.845
[11 empty] | 8 | 7.725
[11 empty] | 10 | 9.625
Copper- Type M
[11 empty] | 0.75 | 0.811
[11 empty] | 1 | 1.055
[11 empty] | 1.25 | 1.291
[11 empty] | 1.5 | 1.527
[11 empty] | 2 | 2.009
[11 empty] | 2.5 | 2.495
[11 empty] | 3 | 2.981
[11 empty] | 3.5 | 3.459
[11 empty] | 4 | 3.935
[11 empty] | 5 | 4.907
[11 empty] | 6 | 5.881
[11 empty] | 8 | 7.785
[11 empty] | 10 | 9.701
CPVC
[11 empty] | 0.75 | 0.874
[11 empty] | 1 | 1.101
[11 empty] | 1.25 | 1.394
[11 empty] | 1.5 | 1.598
[11 empty] | 2 | 2.003
[11 empty] | 2.5 | 2.423
[11 empty] | 3 | 2.95
Cement Lined-Ductil Iron-52
[11 empty] | 3 | 3.28
[11 empty] | 4 | 4.1
[11 empty] | 6 | 6.16
[11 empty] | 8 | 8.27
[11 empty] | 10 | 10.28
[11 empty] | 12 | 12.34

## Equivalent K Factor
www.nsvsoft.net
Enter Values in Green Cells | [6 empty] | Most Remote Sprinkler
Select Values of Blue Cells | [6 empty] | Area of Coverage (ft²) |  |  | 120
[7 empty] | Desnsity (gpm/ft²) |  |  | 0.2
Node 1 | Elev 1 (ft) | K Factor | Flow | Hose Stream Allowance (gpm) | Pipe Type | Nominal ID | Fitting(s) Eqv. Length (ft) | L (ft) | C Factor | Total (Pt) | Equivalent K Factor
Node 2 | Elev 2 (ft) |  | Tot. Flow |  |  | Actual ID |  | F (ft) | Pf (psi/ft) | Elev (Pe)
[8 empty] | T (ft) |  | Frict (pf)
107 | 9 | 8 | 24 | 0 | SCH40 | 1.25 | 0 | 12 | 120 | 9 | 7.7559
108 | 9 |  | 24 |  |  | 1.38 | 0 | 0 | 0.047955 | 0
[7 empty] | 0 | 12 |  | 0.57546
108 | 9 | 8 | 24.7554 | 0 | SCH40 | 1.5 | 4 | 18 | 120 | 9.5755 | 14.0189
C3 | 9 |  | 48.7554 |  |  | 1.61 | 8 | 12 | 0.083995 | 0
[7 empty] | 0 | 30 |  | 2.5198
103 | 9 | 8 | 27.8226 | 0 | SCH40 | 1.5 | 8 | 18 | 120 | 12.0953 | 17.8827
C1 | 8 |  | 76.578 |  |  | 1.61 | 4 | 12 | 0.19364 | 0.433
[7 empty] | 0 | 30 |  | 5.8093
4 | 19.25 | 5.6 | 23.9806 | 0 | SCH40 | 1.5 | 8 | 8.5 | 120 | 18.3376 | 20.688
TR1 | 19.25 |  | 100.5586 |  |  | 1.61 | 0 | 8 | 0.32054 | 0
[7 empty] | 0 | 16.5 |  | 5.289
TR1 | 19.25 | 5.55 | 26.977 | 0 | SCH40 | 1.5 | 8 | 2 | 120 | 23.6266 | 23.494
BR1 | 17.25 |  | 127.5356 |  |  | 1.61 | 0 | 8 | 0.49754 | 0.866
[7 empty] | 0 | 10 |  | 4.9754
BR1 | 17.25 | 0 | 0 | 50 | SCH10 | 3 | 0 | 12 | 120 | 29.468 | 32.5097
BR2 | 17.25 |  | 177.5356 |  |  | 3.26 |  | 0 | 0.029543 | 0
[8 empty] | 12 |  | 0.35452
BR2 | 17.25 | 21.92 | 119.7051 | 0 | SCH10 | 3 | 0 | 70 | 120 | 29.8225 | 47.4135
C1 | 7.75 |  | 297.2407 |  |  | 3.26 | 0 | 0 | 0.076654 | 4.1135
[7 empty] | 0 | 70 |  | 5.3658
C1 | 7.75 | 0 | 0 | 0 | SCH10 | 3 | 7 | 119 | 120 | 39.3018 | 40.7871
C2 | 1 |  | 297.2407 |  |  | 3.26 | 1 | 23 | 0.076654 | 2.9228
[7 empty] | 15 | 142 |  | 10.8848
C2 | 1 | 0 | 0 | 0 | SCH10 | 3 | 0 | 55 | 150 | 53.1094 | 38.5425
CWM | -4.4 |  | 297.2407 |  |  | 3.26 | 24.4 | 24.4 | 0.050728 | 2.3382
[8 empty] | 79.4 |  | 4.0278
CWM | -4.4 | 0 | 0 | 0 | SCH40 | 3 | 100 | 0 | 120 | 59.4754 | 36.3121
Test | 2 |  | 297.2407 |  |  | 3.068 |  | 100 | 0.10302 | -2.7712
[8 empty] | 100 |  | 10.3019
Test | 0 | 0 | 297.2407 | 200 | SCH10 | 1 | 0 | 0 | 0 | 67.0061
0 | 0 |  | 497.2407 |  |  | 1.097 |  | 0
0
[13 empty] | 40 | SCH40a: |  | 10 | SCH10a:
[13 empty] | 1 | 1.049 |  | 1 | 1.097
[13 empty] | 1.25 | 1.38 |  | 1.25 | 1.442
[13 empty] | 1.5 | 1.61 |  | 1.5 | 1.682
[13 empty] | 2 | 2.067 |  | 2 | 2.157
[13 empty] | 2.5 | 2.469 |  | 2.5 | 2.635
[13 empty] | 3 | 3.068 |  | 3 | 3.26
[13 empty] | 3.5 | 3.548 |  | 3.5 | 3.76
[13 empty] | 4 | 4.026 |  | 4 | 4.26
[13 empty] | 5 | 5.047 |  | 5 | 5.295
[13 empty] | 6 | 6.065 |  | 6 | 6.357
[13 empty] | 8 | 7.981 |  | 8 | 8.249
[14 empty] | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
[13 empty] | SCH 10 | 0.674 | 0.884 | 1.097 | 1.442 | 1.682 | 2.157 | 2.635 | 3.26 | 3.76 | 4.26 | 5.295 | 6.357 | 8.249 | 10.37 | 12.09 | 64.212
[13 empty] | SCH 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.071 | 10.14 | 0 | 18.211
[13 empty] | SCH 40 | 0.622 | 0.824 | 1.049 | 1.38 | 1.61 | 2.067 | 2.469 | 3.068 | 3.548 | 4.026 | 5.047 | 6.065 | 7.981 | 10.02 | 11.938 | 61.714
[13 empty] | Copper- Type K | 0 | 0.745 | 0.995 | 1.245 | 1.481 | 1.959 | 2.435 | 2.907 | 3.385 | 3.857 | 4.805 | 5.741 | 7.583 | 9.449 | 0 | 46.587
[13 empty] | Copper- Type L | 0 | 0.785 | 1.025 | 1.265 | 1.505 | 1.985 | 2.465 | 2.945 | 3.425 | 3.905 | 4.875 | 5.845 | 7.725 | 9.625 | 0 | 47.375
[13 empty] | Copper- Type M | 0 | 0.811 | 1.055 | 1.291 | 1.527 | 2.009 | 2.495 | 2.981 | 3.459 | 3.935 | 4.907 | 5.881 | 7.785 | 9.701 | 0 | 47.837
[13 empty] | CPVC | 0 | 0.874 | 1.101 | 1.394 | 1.598 | 2.003 | 2.423 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.343
[13 empty] | SCH 10 |  |  | SCH 30 |  |  | SCH 40 |  |  | Copper- Type K |  |  | Copper- Type L |  |  |  | Copper- Type M |  | CPVC |  | Cement Lined-Ductil Iron-52
[12 empty] | 0.5 | 0.674 |  | 0.5 | 0 |  | 0.5 | 0.622 |  | 0.5 | 0 |  | 0.5 | 0 |  |  | 0.5 | 0 | 0.5 | 0 | 0.5 | 0
[12 empty] | 0.75 | 0.884 |  | 0.75 | 0 |  | 0.75 | 0.824 |  | 0.75 | 0.745 |  | 0.75 | 0.785 |  |  | 0.75 | 0.811 | 0.75 | 0.874 | 0.75 | 0
[12 empty] | 1 | 1.097 |  | 1 | 0 |  | 1 | 1.049 |  | 1 | 0.995 |  | 1 | 1.025 |  |  | 1 | 1.055 | 1 | 1.101 | 1 | 0
[12 empty] | 1.25 | 1.442 |  | 1.25 | 0 |  | 1.25 | 1.38 |  | 1.25 | 1.245 |  | 1.25 | 1.265 |  |  | 1.25 | 1.291 | 1.25 | 1.394 | 1.25 | 0
[12 empty] | 1.5 | 1.682 |  | 1.5 | 0 |  | 1.5 | 1.61 |  | 1.5 | 1.481 |  | 1.5 | 1.505 |  |  | 1.5 | 1.527 | 1.5 | 1.598 | 1.5 | 0
[12 empty] | 2 | 2.157 |  | 2 | 0 |  | 2 | 2.067 |  | 2 | 1.959 |  | 2 | 1.985 |  |  | 2 | 2.009 | 2 | 2.003 | 2 | 0
[12 empty] | 2.5 | 2.635 |  | 2.5 | 0 |  | 2.5 | 2.469 |  | 2.5 | 2.435 |  | 2.5 | 2.465 |  |  | 2.5 | 2.495 | 2.5 | 2.423 | 2.5 | 0
[12 empty] | 3 | 3.26 |  | 3 | 0 |  | 3 | 3.068 |  | 3 | 2.907 |  | 3 | 2.945 |  |  | 3 | 2.981 | 3 | 2.95 | 3 | 3.28
[12 empty] | 3.5 | 3.76 |  | 3.5 | 0 |  | 3.5 | 6.548 |  | 3.5 | 3.385 |  | 3.5 | 3.425 |  |  | 3.5 | 3.459 | 3.5 | 0 | 3.5 | 0
[12 empty] | 4 | 4.26 |  | 4 | 0 |  | 4 | 4.026 |  | 4 | 3.857 |  | 4 | 3.905 |  |  | 4 | 3.935 | 4 | 0 | 4 | 4.16
[12 empty] | 5 | 5.295 |  | 5 | 0 |  | 5 | 5.047 |  | 5 | 4.805 |  | 5 | 4.875 |  |  | 5 | 4.907 | 5 | 0 | 5 | 0
[12 empty] | 6 | 6.357 |  | 6 | 0 |  | 6 | 6.065 |  | 6 | 5.741 |  | 6 | 5.845 |  |  | 6 | 5.881 | 6 | 0 | 6 | 6.28
[12 empty] | 8 | 8.249 |  | 8 | 8.071 |  | 8 | 7.981 |  | 8 | 7.583 |  | 8 | 7.725 |  |  | 8 | 7.785 | 8 | 0 | 8 | 8.39
[12 empty] | 10 | 10.37 |  | 10 | 10.14 |  | 10 | 10.02 |  | 10 | 9.449 |  | 10 | 9.625 |  |  | 10 | 9.701 | 10 | 0 | 10 | 10.4
[12 empty] | 12 | 12.09 |  | 12 | 0 |  | 12 | 11.938 |  | 12 | 0 |  | 12 | 0 |  |  | 12 | 0 | 12 | 0 | 12 | 12.46
SCH 30
[12 empty] | 8 | 8.071
[12 empty] | 10 | 10.14
[12 empty] | 12 | 0
SCH 40
[12 empty] | 0.5 | 0.622
[12 empty] | 0.75 | 0.824
[12 empty] | 1 | 1.049
[12 empty] | 1.25 | 1.38
[12 empty] | 1.5 | 1.61
[12 empty] | 2 | 2.067
[12 empty] | 2.5 | 2.469
[12 empty] | 3 | 3.068
[12 empty] | 3.5 | 3.548
[12 empty] | 4 | 4.026
[12 empty] | 5 | 5.047
[12 empty] | 6 | 6.065
[12 empty] | 8 | 7.981
[12 empty] | 10 | 10.02
[12 empty] | 12 | 11.938
Copper- Type K
[12 empty] | 0.75 | 0.745
[12 empty] | 1 | 0.995
[12 empty] | 1.25 | 1.245
[12 empty] | 1.5 | 1.481
[12 empty] | 2 | 1.959
[12 empty] | 2.5 | 2.435
[12 empty] | 3 | 2.907
[12 empty] | 3.5 | 3.385
[12 empty] | 4 | 3.857
[12 empty] | 5 | 4.805
[12 empty] | 6 | 5.741
[12 empty] | 8 | 7.583
[12 empty] | 10 | 9.449
Copper- Type L
[12 empty] | 0.75 | 0.785
[12 empty] | 1 | 1.025
[12 empty] | 1.25 | 1.265
[12 empty] | 1.5 | 1.505
[12 empty] | 2 | 1.985
[12 empty] | 2.5 | 2.465
[12 empty] | 3 | 2.945
[12 empty] | 3.5 | 3.425
[12 empty] | 4 | 3.905
[12 empty] | 5 | 4.875
[12 empty] | 6 | 5.845
[12 empty] | 8 | 7.725
[12 empty] | 10 | 9.625
Copper- Type M
[12 empty] | 0.75 | 0.811
[12 empty] | 1 | 1.055
[12 empty] | 1.25 | 1.291
[12 empty] | 1.5 | 1.527
[12 empty] | 2 | 2.009
[12 empty] | 2.5 | 2.495
[12 empty] | 3 | 2.981
[12 empty] | 3.5 | 3.459
[12 empty] | 4 | 3.935
[12 empty] | 5 | 4.907
[12 empty] | 6 | 5.881
[12 empty] | 8 | 7.785
[12 empty] | 10 | 9.701
CPVC
[12 empty] | 0.75 | 0.874
[12 empty] | 1 | 1.101
[12 empty] | 1.25 | 1.394
[12 empty] | 1.5 | 1.598
[12 empty] | 2 | 2.003
[12 empty] | 2.5 | 2.423
[12 empty] | 3 | 2.95
Cement Lined-Ductil Iron-52
[12 empty] | 3 | 3.28
[12 empty] | 4 | 4.1
[12 empty] | 6 | 6.16
[12 empty] | 8 | 8.27
[12 empty] | 10 | 10.28
[12 empty] | 12 | 12.34

## Equivalent Length
www.nsvsoft.net
| C factor | 140
| Pipe Type | Cement Lined Ductil 52
[14 empty] | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
[13 empty] | Elbow 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5245 | 0 | 7.366 | 0 | 10.042 | 14.234 | 16.5739 | 20.3162
[13 empty] | Elbow 90 Standard | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8905 | 0 | 18.415 | 0 | 20.0841 | 28.468 | 33.1478 | 42.1952
[13 empty] | Elbow 90 Long Turn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2075 | 0 | 11.049 | 0 | 12.9112 | 20.5602 | 24.1075 | 28.1302
[13 empty] | Tee or Cross | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.6225 | 0 | 36.83 | 0 | 43.0373 | 55.3544 | 75.336 | 93.7672
[13 empty] | Butterfly valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.415 | 0 | 22.098 | 0 | 14.3458 | 18.9787 | 28.6277 | 32.8185
[13 empty] | Gate Valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8415 | 0 | 3.683 | 0 | 4.3037 | 6.3262 | 7.5336 | 9.3767
[13 empty] | Flow switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.513 | 0 | 55.245 | 0 | 22.9532 | 34.7942 | 43.6949 | 56.2603
[13 empty] | Swing check valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.464 | 0 | 40.513 | 0 | 45.9064 | 71.17 | 82.8696 | 101.5811
C factor | 140
Pipe | Cement Lined Ductil 52
Internal Diameter
|  |  | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12" |  |  | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
|  | Elbow 45 | 0 | 1 | 1 | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 5 | 7 | 9 | 11 | 13 |  | SCH 10 | 0.674 | 0.884 | 1.097 | 1.442 | 1.682 | 2.157 | 2.635 | 3.26 | 3.76 | 4.26 | 5.295 | 6.357 | 8.249 | 10.37 | 12.09
|  | Elbow 90 Standard | 1 | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 18 | 22 | 27 |  | SCH 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.071 | 10.14 | 0
|  | Elbow 90 Long Turn | 0.5 | 1 | 2 | 2 | 2 | 3 | 4 | 5 | 5 | 6 | 8 | 9 | 13 | 16 | 18 |  | SCH 40 | 0.622 | 0.824 | 1.049 | 1.38 | 1.61 | 2.067 | 2.469 | 3.068 | 3.548 | 4.026 | 5.047 | 6.065 | 7.981 | 10.02 | 11.938
|  | Tee or Cross | 3 | 4 | 5 | 6 | 8 | 10 | 12 | 15 | 17 | 20 | 25 | 30 | 35 | 50 | 60 |  | Copper- Type K | 0 | 0.745 | 0.995 | 1.245 | 1.481 | 1.959 | 2.435 | 2.907 | 3.385 | 3.857 | 4.805 | 5.741 | 7.583 | 9.449 | 0
|  | Butterfly valve | 0 | 0 | 0 | 0 | 0 | 6 | 7 | 10 | 0 | 12 | 9 | 10 | 12 | 19 | 21 |  | Copper- Type L | 0 | 0.785 | 1.025 | 1.265 | 1.505 | 1.985 | 2.465 | 2.945 | 3.425 | 3.905 | 4.875 | 5.845 | 7.725 | 9.625 | 0
|  | Gate Valve | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 4 | 5 | 6 |  | Copper- Type M | 0 | 0.811 | 1.055 | 1.291 | 1.527 | 2.009 | 2.495 | 2.981 | 3.459 | 3.935 | 4.907 | 5.881 | 7.785 | 9.701 | 0
|  | Flow switch | 0 | 0 | 6 | 9 | 10 | 14 | 17 | 22 | 0 | 30 | 0 | 16 | 22 | 29 | 36 |  | CPVC | 0 | 0.874 | 1.101 | 1.394 | 1.598 | 2.003 | 2.423 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Swing check valve | 0 | 0 | 5 | 7 | 9 | 11 | 14 | 16 | 19 | 22 | 27 | 32 | 45 | 55 | 65 |  | Cement Lined Ductil 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 0 | 4.1 | 0 | 6.16 | 8.27 | 10.28 | 12.34
C Factor |  |  | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
1.33 |  | Elbow 45 | 0 | 1.33 | 1.33 | 1.33 | 2.66 | 2.66 | 3.99 | 3.99 | 3.99 | 5.32 | 6.65 | 9.31 | 11.97 | 14.63 | 17.29
1.33 |  | Elbow 90 Standard | 1.33 | 2.66 | 2.66 | 3.99 | 5.32 | 6.65 | 7.98 | 9.31 | 10.64 | 13.3 | 15.96 | 18.62 | 23.94 | 29.26 | 35.91
1.33 |  | Elbow 90 Long Turn | 0.665 | 1.33 | 2.66 | 2.66 | 2.66 | 3.99 | 5.32 | 6.65 | 6.65 | 7.98 | 10.64 | 11.97 | 17.29 | 21.28 | 23.94
1.33 |  | Tee or Cross | 3.99 | 5.32 | 6.65 | 7.98 | 10.64 | 13.3 | 15.96 | 19.95 | 22.61 | 26.6 | 33.25 | 39.9 | 46.55 | 66.5 | 79.8
1.33 |  | Butterfly valve | 0 | 0 | 0 | 0 | 0 | 7.98 | 9.31 | 13.3 | 0 | 15.96 | 11.97 | 13.3 | 15.96 | 25.27 | 27.93
1.33 |  | Gate Valve | 0 | 0 | 0 | 0 | 0 | 1.33 | 1.33 | 1.33 | 1.33 | 2.66 | 2.66 | 3.99 | 5.32 | 6.65 | 7.98
1.33 |  | Flow switch | 0 | 0 | 7.98 | 11.97 | 13.3 | 18.62 | 22.61 | 29.26 | 0 | 39.9 | 0 | 21.28 | 29.26 | 38.57 | 47.88
1.33 |  | Swing check valve | 0 | 0 | 6.65 | 9.31 | 11.97 | 14.63 | 18.62 | 21.28 | 25.27 | 29.26 | 35.91 | 42.56 | 59.85 | 73.15 | 86.45
(D/D40)^4.87
|  |  | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12" |  |  | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
|  | Elbow 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1538 | 0 | 5.5383 | 0 | 7.5504 | 10.7023 | 12.4616 | 15.2754 |  | SCH 10 | 1.4785 | 1.4082 | 1.2435 | 1.2387 | 1.2375 | 1.2307 | 1.3729 | 1.344 | 1.3266 | 1.3167 | 1.2632 | 1.2573 | 1.1745 | 1.182 | 1.0636
|  | Elbow 90 Standard | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6921 | 0 | 13.8459 | 0 | 15.1008 | 21.4045 | 24.9232 | 31.7257 |  | SCH 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0561 | 1.0597 | 0
|  | Elbow 90 Long Turn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9229 | 0 | 8.3075 | 0 | 9.7077 | 15.4588 | 18.1259 | 21.1505 |  | SCH 40 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Tee or Cross | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.7688 | 0 | 27.6917 | 0 | 32.3589 | 41.6199 | 56.6436 | 70.5017 |  | Copper- Type K | 0 | 0.61212 | 0.77308 | 0.60571 | 0.66583 | 0.77002 | 0.9347 | 0.76912 | 0.7953 | 0.81152 | 0.78718 | 0.76539 | 0.77948 | 0.75146 | 0
|  | Butterfly valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8459 | 0 | 16.615 | 0 | 10.7863 | 14.2697 | 21.5246 | 24.6756 |  | Copper- Type L | 0 | 0.78968 | 0.89341 | 0.65459 | 0.72005 | 0.82108 | 0.99213 | 0.81933 | 0.84213 | 0.8619 | 0.84463 | 0.83532 | 0.85319 | 0.82212 | 0
|  | Gate Valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3846 | 0 | 2.7692 | 0 | 3.2359 | 4.7566 | 5.6644 | 7.0502 |  | Copper- Type M | 0 | 0.92548 | 1.0282 | 0.72277 | 0.77278 | 0.87057 | 1.0523 | 0.86928 | 0.88363 | 0.89463 | 0.87197 | 0.86068 | 0.88595 | 0.85422 | 0
|  | Flow switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.4609 | 0 | 41.5376 | 0 | 17.2581 | 26.1611 | 32.8533 | 42.301 |  | CPVC | 0 | 1.3323 | 1.2657 | 1.0504 | 0.96422 | 0.85798 | 0.91248 | 0.82613 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Swing check valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.1534 | 0 | 30.4609 | 0 | 34.5161 | 53.5113 | 62.3079 | 76.3768 |  | Cement Lined Ductil 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3846 | 0 | 1.0928 | 0 | 1.0786 | 1.1891 | 1.1329 | 1.175
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
1.33 |  |  | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33
|  |  | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
|  | Elbow 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5245 | 0 | 7.366 | 0 | 10.042 | 14.234 | 16.5739 | 20.3162
|  | Elbow 90 Standard | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8905 | 0 | 18.415 | 0 | 20.0841 | 28.468 | 33.1478 | 42.1952
|  | Elbow 90 Long Turn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2075 | 0 | 11.049 | 0 | 12.9112 | 20.5602 | 24.1075 | 28.1302
|  | Tee or Cross | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.6225 | 0 | 36.83 | 0 | 43.0373 | 55.3544 | 75.336 | 93.7672
|  | Butterfly valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.415 | 0 | 22.098 | 0 | 14.3458 | 18.9787 | 28.6277 | 32.8185
|  | Gate Valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8415 | 0 | 3.683 | 0 | 4.3037 | 6.3262 | 7.5336 | 9.3767
|  | Flow switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.513 | 0 | 55.245 | 0 | 22.9532 | 34.7942 | 43.6949 | 56.2603
|  | Swing check valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.464 | 0 | 40.513 | 0 | 45.9064 | 71.17 | 82.8696 | 101.5811

## Multipliers
www.nsvsoft.net
Internal Diameter Multiplier
Pipe Type | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12"
SCH 10 | 1.4785 | 1.4082 | 1.2435 | 1.2387 | 1.2375 | 1.2307 | 1.3729 | 1.344 | 1.3266 | 1.3167 | 1.2632 | 1.2573 | 1.1745 | 1.182 | 1.0636
SCH 30 | - | - | - | - | - | - | - | - | - | - | - | - | 1.0561 | 1.0597 | -
SCH 40 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Copper- Type K | - | 0.61212 | 0.77308 | 0.60571 | 0.66583 | 0.77002 | 0.9347 | 0.76912 | 0.7953 | 0.81152 | 0.78718 | 0.76539 | 0.77948 | 0.75146 | -
Copper- Type L | - | 0.78968 | 0.89341 | 0.65459 | 0.72005 | 0.82108 | 0.99213 | 0.81933 | 0.84213 | 0.8619 | 0.84463 | 0.83532 | 0.85319 | 0.82212 | -
Copper- Type M | - | 0.92548 | 1.0282 | 0.72277 | 0.77278 | 0.87057 | 1.0523 | 0.86928 | 0.88363 | 0.89463 | 0.87197 | 0.86068 | 0.88595 | 0.85422 | -
CPVC | - | 1.3323 | 1.2657 | 1.0504 | 0.96422 | 0.85798 | 0.91248 | 0.82613 | - | - | - | - | - | - | -
Cement Lined Ductil 52 | - | - | - | - | - | - | - | 1.3846 | - | 1.0928 | 0 | 1.0786 | 1.1891 | 1.1329 | 1.175
C factor | 120
C Value Multiplier | 1